{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":41,"n_cols":11,"rows_kept":41,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","BS-Q14AV1B"]
[]
[]
[]
[]
["","","","","","BS10Q14AV1B","BS12Q14AV1B","BS16Q14AV1B","BS4Q14AV1B","BS6Q14AV1B","BS8Q14AV1B"]
["Maximum capacity index of connectable indoor units","","","","","750","750","750","400","600","750"]
["Maximum capacity index of connectable indoor units per branch","","","","","140","140","140","140","140","140"]
["Number of branches","","","","","10","12","16","4","6","8"]
["Maximum number of connectable indoor units","","","","","50","60","64","20","30","40"]
["Maximum number of connectable indoor units per branch","","","","","5","5","5","5","5","5"]
["Dimensions","Unit","","Height","mm","298","298","298","298","298","298"]
["","","","Width","mm","820","820","1060","370","580","580"]
["","","","Depth","mm","430","430","430","430","430","430"]
["Weight","Unit","","","kg","35.0","38.0","50.0","17.0","24.0","26.0"]
["Piping connections","Outdoor unit","Liquid","OD","mm","15.9","15.9, 19.1 (1)","19.1","9.5","12.7","12.7, 15.9 (1)"]
["","","Gas","OD","mm","28.6, 34.9 (1)","28.6, 34.9 (1)","34.9","22.2, 19.1 (1)","28.6, 22.2 (1)","28.6"]
["","","Discharge gas","OD","mm","28.6","28.6","28.6","19.1, 15.9 (1)","19.1, 22.2 (1)","19.1, 22.2 (1), 28.6 (1)"]
["","Indoor unit","Liquid","OD","mm","6.4 (2), 9.5 (3)","6.4 (2), 9.5 (3)","6.4 (2), 9.5 (3)","6.4 (2), 9.5 (3)","6.4 (2), 9.5 (3)","6.4 (2), 9.5 (3)"]
["","","Gas","OD","mm","12.7 (2), 15.9 (3)","12.7 (2), 15.9 (3)","12.7 (2), 15.9 (3)","12.7 (2), 15.9 (3)","12.7 (2), 15.9 (3)","12.7 (2), 15.9 (3)"]
["Standard Accessories","Insulation tube","","","","1","1","1","1","1","1"]
["","Accessory pipe","","","","1","1","1","1","1","1"]
["","Stopper pipes","","","","1","1","1","","1","1"]
["","Insulation tube for stopper pipes","","","","1","1","1","","1","1"]
["","Clamps","","","","1","1","1","1","1","1"]
["","Metal clamp for drain hose","","","","1","1","1","1","1","1"]
["","Sealing material","","","","1","1","1","1","1","1"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240","220-240"]
["Notes","","","","","(1) - Diameter when using the attached reducer. If the joint does not fit, a reducer is requested (field supply).","(1) - Diameter when using the attached reducer. If the joint does not fit, a reducer is requested (field supply).","(1) - Diameter when using the attached reducer. If the joint does not fit, a reducer is requested (field supply).","(1) - Diameter when using the attached reducer. If the joint does not fit, a reducer is requested (field supply).","(1) - Diameter when using the attached reducer. If the joint does not fit, a reducer is requested (field supply).","(1) - Diameter when using the attached reducer. If the joint does not fit, a reducer is requested (field supply)."]
["","","","","","(2) - When connecting indoor units smaller or equal to 50 class (no need to cut the outlet pipe)","(2) - When connecting indoor units smaller or equal to 50 class (no need to cut the outlet pipe)","(2) - When connecting indoor units smaller or equal to 50 class (no need to cut the outlet pipe)","(2) - When connecting indoor units smaller or equal to 50 class (no need to cut the outlet pipe)","(2) - When connecting indoor units smaller or equal to 50 class (no need to cut the outlet pipe)","(2) - When connecting indoor units smaller or equal to 50 class (no need to cut the outlet pipe)"]
["","","","","","(3) - When connecting indoor units larger or equal to 63 class (the outlet pipe needs to be cut)","(3) - When connecting indoor units larger or equal to 63 class (the outlet pipe needs to be cut)","(3) - When connecting indoor units larger or equal to 63 class (the outlet pipe needs to be cut)","(3) - When connecting indoor units larger or equal to 63 class (the outlet pipe needs to be cut)","(3) - When connecting indoor units larger or equal to 63 class (the outlet pipe needs to be cut)","(3) - When connecting indoor units larger or equal to 63 class (the outlet pipe needs to be cut)"]
["","","","","","(4) - Insulators are necessary (field supply) for the triple piping side","(4) - Insulators are necessary (field supply) for the triple piping side","(4) - Insulators are necessary (field supply) for the triple piping side","(4) - Insulators are necessary (field supply) for the triple piping side","(4) - Insulators are necessary (field supply) for the triple piping side","(4) - Insulators are necessary (field supply) for the triple piping side"]
["","","","","","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA"]
["","","","","","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A"]
["","","","","","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA"]
["","","","","","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker"]