{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":7,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAA-DW1P-H"]
[]
[]
[]
[]
["","","","","","EWAA014DAW1P-H-","EWAA016DAW1P-H-"]
["Sound pressure level","Cooling","","Nom.","dBA","50.8","51.0"]
["Hydraulic components","Expansion vessel","","Volume","l","8","8"]
["Operation range","Air side","Cooling","Min.","°CDB","10","10"]
["","","","Max.","°CDB","43","43"]
["","Water side","Cooling","Max.","°CDB","22","22"]
["","","","Min.","°CDB","5","5"]
["Refrigerant charge","Per circuit","","","kg","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6"]
["Compressor","Type","","","","Hermetically sealed swing inverter compressor","Hermetically sealed swing inverter compressor"]
["","Starting method","","","","Inverter driven","Inverter driven"]
["","Quantity","","","","1","1"]
["Weight","Unit","","","kg","147","147"]
["Air heat exchanger","Type","","","","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler"]
["EER","","","","","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Refrigerant","GWP","","","","675.0","675.0"]
["","Type","","","","R-32","R-32"]
["","Circuits","","Quantity","","1","1"]
["","Control","","","","Electronic expansion valve","Electronic expansion valve"]
["Fan motor","Speed","Cooling","Nom.","rpm","650","650"]
["Cooling capacity","Nom.","","","kW","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Water heat exchanger","Water volume","","","l","2","2"]
["","Minimum water volume in the system","","","l","20 (6)","20 (6)"]
["","Type","","","","Plate heat exchanger","Plate heat exchanger"]
["Power input","Cooling","","Nom.","kW","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["Sound power level","Cooling","","Nom.","dBA","69.0","69.0"]
["Dimensions","Unit","","Width","mm","1,380","1,380"]
["","","","Depth","mm","460","460"]
["","","","Height","mm","870","870"]
["Capacity control","Method","","","","Variable (inverter)","Variable (inverter)"]
["Fan","Air flow rate","Cooling","Nom.","m³/min","85","85"]
["Compressor","Starting method","","","","Inverter","Inverter"]
["Power supply","Phase","","","","3~","3~"]
["","Name","","","","W1","W1"]
["","Frequency","","","Hz","50","50"]
["","Voltage","","","V","400","400"]
["Notes","","","","","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB"]
["","","","","","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB"]
["","","","","","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - According to EN14825","(5) - According to EN14825"]
["","","","","","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual."]
["","","","","","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing"]