{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":45,"n_cols":15,"rows_kept":45,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-D-XS"]
[]
[]
[]
[]
["","","","","EWAD250D-XS","EWAD280D-XS","EWAD300D-XS","EWAD330D-XS","EWAD350D-XS","EWAD380D-XS","EWAD400D-XS","EWAD470D-XS","EWAD520D-XS","EWAD580D-XS","EWAD620D-XS"]
["Sound pressure level","Cooling","Nom.","dBA","78 (2)","78 (2)","78 (2)","78 (2)","78 (2)","79 (2)","79 (2)","79 (2)","79 (2)","79 (2)","79 (2)"]
["Refrigerant charge","Per circuit","","kg","29.0","33.0","35.0","38.0","35.0","35.0","39.0","42.0","45.0","45.0","50.0"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","TCO2Eq","41.5","47.2","50.1","54.3","50.1","50.1","55.8","60.1","64.4","64.4","71.5"]
["Compressor","Type","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Asymmetric single screw compressor","Asymmetric single screw compressor","Asymmetric single screw compressor"]
["","Quantity","","","2","2","2","2","2","2","2","2","2","2","2"]
["Weight","Operation weight","","kg","3,000","3,400","3,400","3,400","3,400","3,400","3,400","3,780","4,940","4,940","4,940"]
["","Unit","","kg","2,905","3,285","3,285","3,235","3,240","3,240","3,240","3,510","4,670","4,685","4,685"]
["Air heat exchanger","Type","","","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler","High efficiency fin and tube type with integral subcooler"]
["EER","","","","3.07 (1)","3.11 (1)","3.15 (1)","3.10 (1)","3.06 (1)","3.08 (1)","3.10 (1)","3.07 (1)","3.09 (1)","3.12 (1)","3.16 (1)"]
["ESEER","","","","3.45","3.49","3.51","3.73","3.56","3.47","3.48","3.72","3.88","3.89","3.75"]
["Refrigerant","GWP","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Type","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","Circuits","Quantity","","2","2","2","2","2","2","2","2","2","2","2"]
["Cooling capacity","Nom.","","kW","246 (1)","274 (1)","300 (1)","326 (1)","350 (1)","374 (1)","399 (1)","467 (1)","522 (1)","573 (1)","620 (1)"]
["Water heat exchanger","Water volume","","l","95","115","115","165","160","160","160","270","270","255","255"]
["","Type","","","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube","Single pass shell & tube"]
["Power input","Cooling","Nom.","kW","80.1 (1)","88.2 (1)","95.4 (1)","105 (1)","114 (1)","121 (1)","129 (1)","152 (1)","169 (1)","183 (1)","196 (1)"]
["Sound power level","Cooling","Nom.","dBA","97","97","97","97","97","99","99","99","99","99","99"]
["Dimensions","Unit","Width","mm","2,234","2,234","2,234","2,234","2,234","2,234","2,234","2,234","2,234","2,234","2,234"]
["","","Depth","mm","3,138","4,040","4,040","4,040","4,040","4,040","4,040","4,040","4,940","4,940","4,940"]
["","","Height","mm","2,355","2,355","2,355","2,355","2,355","2,355","2,355","2,223","2,223","2,223","2,223"]
["Capacity control","Minimum capacity","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["","Method","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["Fan","Air flow rate","Nom.","l/s","22,302","30,591","29,736","29,736","29,736","43,001","42,306","43,696","54,620","54,620","54,620"]
["","Speed","","rpm","900","900","900","900","900","890","890","890","890","890","890"]
["Compressor","Starting method","","","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta"]
["Power supply","Phase","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","Hz","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","V","400","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation.","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation."]
["","","","","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744","(2) - Sound pressure levels are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C; full load operation; Standard: ISO3744"]
["","","","","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %","(4) - Maximum starting current: starting current of biggest compressor + 75 % of maximum current of the other compressor + fans current for the circuit at 75 %"]
["","","","","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(5) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current."]
["","","","","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(6) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(7) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(8) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water","(9) - Fluid: Water"]
["","","","","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(10) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]