{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":64,"n_cols":11,"rows_kept":64,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAH-TZPSB"]
[]
[]
[]
[]
["","","","","","EWAH370TZPSB2","EWAH440TZPSB2","EWAH530TZPSB2","EWAH610TZPSB2","EWAH690TZPSB2","EWAH770TZPSB2"]
["Cooling capacity","Nom.","","","kW","371","435","532","606","692","779"]
["Capacity control","Method","","","","Variable","Variable","Variable","Variable","Variable","Variable"]
["","Minimum capacity","","","%","16.7","14.3","11.7","10","10","12.8"]
["Power input","Cooling","","Nom.","kW","102","121","137","163","186","217"]
["EER","","","","","3.62","3.58","3.86","3.7","3.72","3.58"]
["IPLV","","","","","6.15","6.35","6.36","6.35","6.48","6.63"]
["SEER","","","","","5.239","5.417","5.587","5.699","5.855","5.876"]
["Dimensions","Unit","","Depth","mm","7,683","9,483","7,683","8,583","9,483","11,283"]
["","","","Height","mm","2,537","2,537","2,537","2,537","2,537","2,537"]
["","","","Width","mm","2,258","2,258","2,258","2,258","2,258","2,258"]
["Weight","Operation weight","","","kg","5,982.4","7,023","6,656.8","7,636.2","8,289.4","8,661.2"]
["","Unit","","","kg","5,741.4","6,722","6,364.8","7,140.2","7,804.4","8,208.2"]
["Casing","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["Air heat exchanger","Type","","","","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel","Microchannel"]
["Fan","Quantity","","","","16","20","16","18","22","24"]
["","Type","","","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller"]
["Fan motor","Drive","","","","Brushless","Brushless","Brushless","Brushless","Brushless","Brushless"]
["Compressor","Quantity","","","","2","2","2","2","2","2"]
["","Type","","","","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor"]
["","Starting method","","","","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven","Inverter driven"]
["Operation range","Air side","Cooling","Min.","°CDB","-18","-18","-18","-18","-18","-18"]
["","","","Max.","°CDB","55","55","55","55","55","55"]
["","Water side","Evaporator","Min.","°CDB","-8","-8","-8","-8","-8","-8"]
["","","","Max.","°CDB","18","18","18","18","18","18"]
["Sound power level","Cooling","","Nom.","dBA","100.3","100.8","103.24","104.21","104.24","103.7"]
["Sound pressure level","Cooling","","Nom.","dBA","78.85","78.75","81.78","82.45","82.2","81.14"]
["Refrigerant","Type","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["","GWP","","","","7","7","7","7","7","7"]
["","Circuits","","Quantity","","2","2","2","2","2","2"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","168.3mm","168.3mm","168.3mm","219.1mm","219.1mm","219.1mm"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~"]
["","Frequency","","","Hz","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400"]
["","Voltage range","","Min.","%","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10"]
["Unit","Running current","Cooling","Nom.","A","175.85","205.4","233.82","272.98","316.97","364.19"]
["","","","Max","A","272","319","350","424","491","536"]
["","Max unit current for wires sizing","","","A","298.9","351.43","384.54","466.74","540.17","589.23"]
["Notes","","","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; ambient 35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0"]
["","","","","","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only","(2) - The value refers to the pressure drop in the evaporator only"]
["","","","","","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1","(3) - Sound power level (referred to evaporator 12/7°C, ambient 35°C full load operation) are measured in accordance with ISO 9614 and Eurovent 8/1"]
["","","","","","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(4) - The sound pressure level is measured via a microphone at 1m distance of the unit."]
["","","","","","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(5) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition"]
["","","","","","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(6) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request."]
["","","","","","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options.","(7) - All data refers to the standard unit without options."]
["","","","","","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(8) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced.","(9) - Maximum starting current: starting current of biggest compressor + current of the other compressors at maximum load + fans current at maximum load. In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current.","(10) - Nominal current in cooling mode: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C. Compressor + fans current."]
["","","","","","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(11) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(12) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(13) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(14) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book"]
["","","","","","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data.","(15) - All data are subject to change without notice. Please refer to the unit nameplate data."]
["","","","","","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(16) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding","(17) - The sound pressure level is calculated from the sound power level and is for information only and not considered binding"]
["","","","","","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water","(18) - Fluid: Water"]
["","","","","","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(19) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]