{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":53,"n_cols":7,"rows_kept":53,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAQ-CWH"]
[]
[]
[]
[]
["","","","","","EWAQ016CAWH","EWAQ021CAWH"]
["Operation range","Air side","Cooling","Min.","°CDB","-5","-5"]
["","","","Max.","°CDB","43","43"]
["","Water side","Cooling","Max.","°CDB","20","20"]
["","","","Min.","°CDB","-10 (3)","-10 (3)"]
["Refrigerant charge","Per circuit","","","kg","7.60","7.60"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","15.9","15.9"]
["Compressor","Type","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["","Quantity","","","","1","2"]
["Weight","Unit","","","kg","283","336"]
["Air heat exchanger","Type","","","","Air cooled coil","Air cooled coil"]
["EER","","","","","2.93","2.84"]
["ESEER","","","","","4.69","4.58"]
["Refrigerant","GWP","","","","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A"]
["","Circuits","","Quantity","","1","1"]
["","Control","","","","Electronic expansion valve","Electronic expansion valve"]
["Cooling capacity","Nom.","","","kW","17.0 (1)","21.2 (1)"]
["Water heat exchanger","Water volume","","","l","3","3"]
["","Type","","","","Brazed plate","Brazed plate"]
["","Water flow rate","","Min.","l/min","23","23"]
["Power input","Cooling","","Nom.","kW","5.81 (1)","7.47 (1)"]
["Sound power level","Cooling","","Nom.","dBA","78","78"]
["Dimensions","Unit","","Width","mm","1,370","1,370"]
["","","","Depth","mm","774","774"]
["","","","Height","mm","1,684","1,684"]
["Capacity control","Minimum capacity","","","%","25","25"]
["","Method","","","","Inverter controlled","Inverter controlled"]
["Fan","External static pressure","","Max.","Pa","78","78"]
["","Air flow rate","Cooling","Nom.","m³/min","171","185"]
["Water circuit","Total water volume","","","l","4.2 (6)","4.2 (6)"]
["","Drain valve / fill valve","","","","Yes","Yes"]
["","Air purge valve","","","","Yes","Yes"]
["","Piping","","","inch","1-1/4\"","1-1/4\""]
["","Piping connections diameter","","","inch","1-1/4\" (female)","1-1/4\" (female)"]
["","Shut off valve","","","","Yes","Yes"]
["","Safety valve","","","bar","3","3"]
["Power supply","Phase","","","","3N~","3N~"]
["","Name","","","","W1","W1"]
["","Frequency","","","Hz","50","50"]
["","Voltage","","","V","400","400"]
["Notes","","","","","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C","(1) - Cooling: entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; ambient air temp. 35°C"]
["","","","","","(2) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)","(2) - Condition: Ta 35°C - LWE 7°C ( DT = 5°C)"]
["","","","","","(3) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL option)","(3) - Water can be used above 5°C. Between 0°C and 5°C a 30% glycol solution (propylene or ethylene) has to be used. Between 0°C and -10°C a 40% glycol solution (propylene or ethylene) has to be used (see installation manual and information related to OPZL option)"]
["","","","","","(4) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info.","(4) - Excluding water volume in the unit. In most applications this minimum water volume will have a satisfying result. In critical processes or in rooms with a high heat load though, extra water volume might be required. Refer to operation range for more info."]
["","","","","","(5) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop.","(5) - This is PD between inlet & outlet connections of unit. It includes the water side heat exchanger pressure drop."]
["","","","","","(6) - Including piping + PHE; excluding expansion vessel","(6) - Including piping + PHE; excluding expansion vessel"]
["","","","","","(7) - No peak current because of inverter compressor","(7) - No peak current because of inverter compressor"]