{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":74,"n_cols":8,"rows_kept":74,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYQ-ADVP"]
[]
[]
[]
[]
["","","","","","EWYQ005ADVP","EWYQ006ADVP","EWYQ007ADVP"]
["Sound pressure level","Heating","","Nom.","dBA","50 (5)"]
["","Cooling","","Nom.","dBA","50 (5)"]
["Hydraulic components","Expansion vessel","","Volume","l","6"]
["Refrigerant charge","Per circuit","","","kg","1.70"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","3.55"]
["Compressor","Type","","","","Hermetically sealed swing compressor"]
["","Starting method","","","","Inverter driven"]
["","Quantity","","","","1"]
["Weight","Operation weight","","","kg","104"]
["","Unit","","","kg","100"]
["Air heat exchanger","Type","","","","Tube type"]
["EER","","","","","2.72 (1)","2.53 (1)","2.39 (1)"]
["Refrigerant","GWP","","","","2,087.5"]
["","Type","","","","R-410A"]
["","Circuits","","Quantity","","1.00"]
["","Control","","","","Inverter"]
["Cooling capacity","Nom.","","","kW","5.28 (1)"]
["Piping connections","Water heat exchanger drain","","","","5/16 SAE flare"]
["Water heat exchanger","Minimum water volume in the system","","","l","10"]
["","Type","","","","Brazed plate"]
["","Water flow rate","","Min.","l/min","12"]
["Power input","Cooling","","Nom.","kW","1.94 (1)"]
["","Heating","","Nom.","kW","1.65 (2), 2.02 (3)"]
["Sound power level","Cooling","","Nom.","dBA","62.0"]
["COP","","","","","3.65 (2), 2.76 (3)"]
["Dimensions","Unit","","Width","mm","1,190"]
["","","","Depth","mm","360"]
["","","","Height","mm","805"]
["Capacity control","Method","","","","Inverter controlled"]
["Heating capacity","Nom.","","","kW","6.02 (2), 5.57 (3)"]
["Water circuit","Piping connections diameter","","","inch","1\" MBSP"]
["Power supply","Phase","","","","1~"]
["","Name","","","","V3"]
["","Frequency","","","Hz","50"]
["","Voltage","","","V","230"]
["Notes","","","","","(1) - Tamb 35°C - LWE 7°C (DT=5°C)","(1) - Tamb 35°C - LWE 7°C (DT=5°C)","(1) - Tamb 35°C - LWE 7°C (DT=5°C)"]
["","","","","","(2) - DB/WB 7°C/6°C - LWC 35°C (DT=5°C)","(2) - DB/WB 7°C/6°C - LWC 35°C (DT=5°C)","(2) - DB/WB 7°C/6°C - LWC 35°C (DT=5°C)"]
["","","","","","(3) - DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(3) - DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(3) - DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(4) - Including piping + PHE; excluding expansion vessel","(4) - Including piping + PHE; excluding expansion vessel","(4) - Including piping + PHE; excluding expansion vessel"]
["","","","","","(5) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(5) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information.","(5) - The sound pressure level is measured via a microphone at a certain distance from the unit. It is a relative value depending on the distance and acoustic environment. Refer to sound spectrum drawing for more information."]
["","","","","","(6) - Contains fluorinated greenhouse gases"]
["Cooling capacity","Nom.","","","kW","","6.08 (1)","7.18 (1)"]
["Capacity control","Method","","","","","Inverter controlled","Inverter controlled"]
["Power input","Cooling","","Nom.","kW","","2.40 (1)","3.00 (1)"]
["Dimensions","Unit","","Depth","mm","","360","360"]
["","","","Height","mm","","805","805"]
["","","","Width","mm","","1190","1190"]
["Weight","Operation weight","","","kg","","104","104"]
["","Unit","","","kg","","100","100"]
["Casing","Colour","","","","","Ivory white","Ivory white"]
["","Material","","","","","Polyester painted galvanised steel plate","Polyester painted galvanised steel plate"]
["Fan","Quantity","","","","","1","1"]
["","Type","","","","","Propeller fan","Propeller fan"]
["Compressor","Quantity","","","","","1","1"]
["","Type","","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["","Starting method","","","","","Inverter driven","Inverter driven"]
["Operation range","Air side","Cooling","Min.","°CDB","","10","10"]
["","","","Max.","°CDB","","43","43"]
["","Water side","Evaporator","Min.","°CDB","","5.00","5.00"]
["","","","Max.","°CDB","","20","20"]
["Sound power level","Cooling","","Nom.","dBA","","62.0","63.0"]
["Sound pressure level","Cooling","","Nom.","dBA","","50 (5)","50 (5)"]
["Refrigerant","GWP","","","","","2087.5","2087.5"]
["","Circuits","","Quantity","","","1.00","1.00"]
["Power supply","Frequency","","","Hz","","50","50"]
["","Voltage range","","Min.","%","","-10","-10"]
["","","","Max.","%","","10","10"]
["Unit","Running current","","Max","A","","19.0","19.0"]