{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":81,"n_cols":11,"rows_kept":81,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXZA-A"]
[]
[]
[]
[]
["","","","","","FXZA15A2VEB","FXZA20A2VEB","FXZA25A2VEB","FXZA32A2VEB","FXZA40A2VEB","FXZA50A2VEB"]
["Sound pressure level","Heating","","At high fan speed","dBA","31.5","32.0","33.0","33.5","37.0","43.0"]
["","","","At low fan speed","dBA","25.5","25.5","25.5","26.0","28.0","33.0"]
["","","","At medium fan speed","dBA","28.0","29.5","30.0","30.0","32.0","40.0"]
["","Cooling","","At low fan speed","dBA","25.5","25.5","25.5","26.0","28.0","33.0"]
["","","","At high fan speed","dBA","31.5","32.0","33.0","33.5","37.0","43.0"]
["","","","At medium fan speed","dBA","28.0","29.5","30.0","30.0","32.0","40.0"]
["Standard Accessories","Installation and operation manual","","","","1","1","1","1","1","1"]
["","Drain hose","","","","1","1","1","1","1","1"]
["","Metal clamp for drain hose","","","","1","1","1","1","1","1"]
["","Washer for hanger bracket","","","","8","8","8","8","8","8"]
["","Screws","","","","4","4","4","4","4","4"]
["","Insulation for fitting","","","","2","2","2","2","2","2"]
["","Sealing pad","","","","4","4","4","4","4","4"]
["","Clamps","","","","7","7","7","7","7","7"]
["Refrigerant","GWP","","","","675.0","675.0","675.0","675.0","675.0","675.0"]
["","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.018 (1)","0.018 (1)","0.020 (1)","0.019 (1)","0.029 (1)","0.048 (1)"]
["","Heating","","At high fan speed","kW","0.018 (1)","0.018 (1)","0.020 (1)","0.019 (1)","0.029 (1)","0.048 (1)"]
["Cooling capacity","Total capacity","","At high fan speed","kW","1.70","2.20","2.80","3.60","4.50","5.60"]
["Piping connections","Liquid","","OD","mm","6","6","6","6","6","6"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Gas","","OD","mm","9.52","9.52","9.52","9.52","12.70","12.70"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Drain","","","","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)"]
["Decoration panel 4","Dimensions","","Depth","mm","700","700","700","700","700","700"]
["","","","Width","mm","700","700","700","700","700","700"]
["","","","Height","mm","55","55","55","55","55","55"]
["","Model","","","","BYFQ60B3W1, See note 2","BYFQ60B3W1, See note 2","BYFQ60B3W1, See note 2","BYFQ60B3W1, See note 2","BYFQ60B3W1, See note 2","BYFQ60B3W1, See note 2"]
["","Colour","","","","WHITE (RAL9010)","WHITE (RAL9010)","WHITE (RAL9010)","WHITE (RAL9010)","WHITE (RAL9010)","WHITE (RAL9010)"]
["","Weight","","","kg","2.7","2.7","2.7","2.7","2.7","2.7"]
["Sound power level","Cooling","","At high fan speed","dBA","49","49","50","51","54","60"]
["Air filter","Type","","","","Resin net","Resin net","Resin net","Resin net","Resin net","Resin net"]
["Dimensions","Unit","","Width","mm","575","575","575","575","575","575"]
["","","","Depth","mm","575","575","575","575","575","575"]
["","","","Height","mm","260","260","260","260","260","260"]
["Casing","Material","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["Weight","Unit","","","kg","15.5","15.5","15.5","16.5","16.5","18.5"]
["Decoration panel 2","Weight","","","kg","2.8","2.8","2.8","2.8","2.8","2.8"]
["","Model","","","","BYFQ60C4W1S","BYFQ60C4W1S","BYFQ60C4W1S","BYFQ60C4W1S","BYFQ60C4W1S","BYFQ60C4W1S"]
["","Dimensions","","Depth","mm","620","620","620","620","620","620"]
["","","","Width","mm","620","620","620","620","620","620"]
["","","","Height","mm","46","46","46","46","46","46"]
["","Colour","","","","SILVER","SILVER","SILVER","SILVER","SILVER","SILVER"]
["Decoration panel 3","Dimensions","","Depth","mm","700","700","700","700","700","700"]
["","","","Height","mm","55","55","55","55","55","55"]
["","","","Width","mm","700","700","700","700","700","700"]
["","Colour","","","","White (RAL9010)","White (RAL9010)","White (RAL9010)","White (RAL9010)","White (RAL9010)","White (RAL9010)"]
["","Model","","","","BYFQ60B2W1, See note 2","BYFQ60B2W1, See note 2","BYFQ60B2W1, See note 2","BYFQ60B2W1, See note 2","BYFQ60B2W1, See note 2","BYFQ60B2W1, See note 2"]
["","Weight","","","kg","2.7","2.7","2.7","2.7","2.7","2.7"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","8.5","8.7","9.0","10.0","11.5","14.0"]
["","","","At low fan speed","m³/min","6.5","6.5","6.5","7.0","8.0","10.0"]
["Decoration panel","Weight","","","kg","2.8","2.8","2.8","2.8","2.8","2.8"]
["","Model","","","","BYFQ60C4W1W","BYFQ60C4W1W","BYFQ60C4W1W","BYFQ60C4W1W","BYFQ60C4W1W","BYFQ60C4W1W"]
["","Dimensions","","Height","mm","46","46","46","46","46","46"]
["","","","Depth","mm","620","620","620","620","620","620"]
["","","","Width","mm","620","620","620","620","620","620"]
["","Colour","","","","White (N9.5)","White (N9.5)","White (N9.5)","White (N9.5)","White (N9.5)","White (N9.5)"]
["Heating capacity","Total capacity","","At high fan speed","kW","1.90","2.50","3.20","4.00","5.00","6.30"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","6","6","6","6","6","6"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Name","","","","VE","VE","VE","VE","VE","VE"]
["","Frequency","","","Hz","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting."]
["","","","","","(2) - It is necessary to use option ERPS23 (conversion wire harness) for connection of standard panel.","(2) - It is necessary to use option ERPS23 (conversion wire harness) for connection of standard panel.","(2) - It is necessary to use option ERPS23 (conversion wire harness) for connection of standard panel.","(2) - It is necessary to use option ERPS23 (conversion wire harness) for connection of standard panel.","(2) - It is necessary to use option ERPS23 (conversion wire harness) for connection of standard panel.","(2) - It is necessary to use option ERPS23 (conversion wire harness) for connection of standard panel."]
["","","","","","(3) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(3) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(4) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB","(4) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB","(4) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB","(4) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB","(4) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB","(4) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB"]
["","","","","","(5) - Dimensions do not include control box","(5) - Dimensions do not include control box","(5) - Dimensions do not include control box","(5) - Dimensions do not include control box","(5) - Dimensions do not include control box","(5) - Dimensions do not include control box"]
["","","","","","(6) - The sound power level is an absolute value indicating the power which a sound source generates.","(6) - The sound power level is an absolute value indicating the power which a sound source generates.","(6) - The sound power level is an absolute value indicating the power which a sound source generates.","(6) - The sound power level is an absolute value indicating the power which a sound source generates.","(6) - The sound power level is an absolute value indicating the power which a sound source generates.","(6) - The sound power level is an absolute value indicating the power which a sound source generates."]
["","","","","","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(9) - MCA/MFA: MCA = 1.1 x FLA","(9) - MCA/MFA: MCA = 1.1 x FLA","(9) - MCA/MFA: MCA = 1.1 x FLA","(9) - MCA/MFA: MCA = 1.1 x FLA","(9) - MCA/MFA: MCA = 1.1 x FLA","(9) - MCA/MFA: MCA = 1.1 x FLA"]
["","","","","","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker","(10) - Instead of a fuse, use a circuit breaker"]
["","","","","","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA"]
["","","","","","(12) - Contains fluorinated greenhouse gases","(12) - Contains fluorinated greenhouse gases","(12) - Contains fluorinated greenhouse gases","(12) - Contains fluorinated greenhouse gases","(12) - Contains fluorinated greenhouse gases","(12) - Contains fluorinated greenhouse gases"]